## Sheet1
ITEM | DESCRIPTION | UNIT | QTY. | RATE | AMOUNT
1 | DEMOLISHING WORK
Demolish the existing structure and all their
components. The following activities and others
which are necessary to make the site clear and
ready to start and execute new works, are
included in the demolishing work of
dry latrine ,trees and etc..
Careful removal of materials that can be saved.
Storing saved materials where directed by the
engineer and handing over to the employer.
Disposal of the debris in relation with the
demolition.
Cost replacement of recoverable materials, if
damaged due to improper handling by the contractor.
Fell trees, cut the stems in to logs of appropriate size,
trim branches, uproot stumps and hand over to the
employer by piling it where directed by the engineer.
Demolition of sewerage structures such as pipe
lines, manholes etc both visible or concealed from
view and handle it in the like manner as specified
for demolishing work including sub structure.
In the execution of the project the contractors
shall take care not to damage any utility lines that
exist over head, on the ground or in the ground.
The contractor shall be responsible for any damage
| due to his/her negligence. | ls | 1 | 8000 | 8000
| TOTAL TO SUMMARY …………………… | BIRR |  |  | 8000
2 | EXCAVATION & EARTH WORK
Excavation all according to attached soil report .
Bulk excavation
01 | Clear off site to an average depth of 30cm | m² | 1185 | 11.35 | 13449.75
Bulk excavation
02 | To a depth not exceeding200cm | m3 | 3040 | 90.4 | 274816
Pit & Trench excavation
03 | Pit not exceeding 1.5 m | m3 | 1626 | 90.4 | 146990.4
04 | Pit over 1.5 m not exceeding 3 m | m3 | 1084 | 100.45 | 108887.8
05 | Trench not exceeding 1m | m3 | 33 | 93.65 | 3090.45
Fill
Compaction fill shall be every 20 cm thick
until it attains a minimum of 95% proctor density
06 | Selected borrowed fill | m3 | 1874 | 141 | 264234
07 | Selected excavated fill | m3 | 2199 | 72.35 | 159097.65
08 | Disposal | m3 | 5595 | 34.4 | 192468
Sub Base
09 | 25cm thick hard core | m² | 1962 | 156.1 | 306268.2
| TOTAL TO SUMMARY …………………… | BIRR |  |  | 1469302.25
03. CONCRETE WORK
In situ concrete
01 | Plain blinding concrete C-5 | m3 | 44 | 123.3 | 5425.2
| Reinforced sub structure concrete |  |  |  | 0
| Use ordinary Portland cement |  |  |  | 0
02 | C-25 in isolated & continues footing | m3 | 400 | 2281.4 | 912560
03 | C-25 in foundation column | m3 | 53 | 2560.8 | 135722.4
04 | C-25 in concrete foundation wall | m3 | 55 | 2329.75 | 128136.25
05 | C-25 in lift shaft | m3 | 7 | 2345.65 | 16419.55
06 | C-25 in retaining wall | m3 | 208 | 2329.75 | 484588
07 | C-25 in beam | m3 | 134 | 2323.45 | 311342.3
08 | C-20 in ramp | m3 | 4 | 2198.8 | 8795.2
09 | C-20 in slab and entrance steps | m3 | 210 | 2198.8 | 461748
Reinforced super structure concrete
Use ordinary Portland cement
10 | C-25 in elevation column | m3 | 313 | 2352.65 | 736379.45
11 | C-25 in beams | m3 | 146 | 2356.15 | 343997.9
12 | C-25 in sun breaker | m3 | 29 | 2377.35 | 68943.15
13 | C-25 in concrete wall | m3 | 505 | 2340.5 | 1181952.5
14 | C-25 in lift shaft | m3 | 52 | 2366.4 | 123052.8
15 | C-25 in pergola | m3 | 6 | 2852.8 | 17116.8
16 | C-25 in stair case | m3 | 73 | 2360.05 | 172283.65
17 | C-25 in suspended floor & roof slab | m3 | 2082 | 2332.4 | 4856056.8
Form work
Sub structure normal finish to:-
18 | Isolated & continues footing | m² | 570 | 162.85 | 92824.5
19 | Foundation column | m² | 420 | 166.95 | 70119
20 | Concrete wall | m² | 441 | 167.9 | 74043.9
21 | Lift shaft | m² | 56 | 167.9 | 9402.4
22 | Retaining wall | m² | 2077 | 167.9 | 348728.3
23 | Beam | m² | 891 | 173.55 | 154633.05
24 | Ramp | m² | 4 | 201.6 | 806.4
25 | entrance steps | m² | 89 | 201.6 | 17942.4
Super structure normal finish to:-
26 | Elevation column | m² | 2531 | 168.05 | 425334.55
27 | Beams & lintel | m² | 910 | 174.8 | 159068
28 | Sun breaker | m² | 361 | 172.4 | 62236.4
29 | Concrete wall | m² | 3392 | 172.4 | 584780.8
30 | Lift shaft | m² | 416 | 172.4 | 71718.4
31 | Pergola | m² | 72 | 172.4 | 12412.8
32 | Stair case | m² | 391 | 206.9 | 80897.9
33 | Suspended floor & roof slab | m² | 8859 | 182.35 | 1615438.65
Super structure fare faced finish to:-
34 | Concrete wall | m² | 554 | 176.2 | 97614.8
Reinforcement steel bar
Sub structure
35 | Diameter, 24 mm | kg | 2265 | 34.35 | 77802.75
36 | Diameter, 20 mm | kg | 7820 | 34.45 | 269399
37 | Diameter, 16 mm | kg | 12750 | 33.5 | 427125
38 | Diameter, 14 mm | kg | 33650 | 34.55 | 1162607.5
39 | Diameter, 12 mm | kg | 37385 | 35.1 | 1312213.5
40 | Diameter, 10 mm | kg | 6155 | 35.35 | 217579.25
41 | Diameter, 8 mm | kg | 4090 | 35.4 | 144786
Super Structure
42 | Diameter, 24 mm | kg | 2320 | 34.4 | 79808
43 | Diameter, 20 mm | kg | 5665 | 34.55 | 195725.75
44 | Diameter, 16 mm | kg | 45190 | 33.55 | 1516124.5
45 | Diameter, 14 mm | kg | 100430 | 34.6 | 3474878
46 | Diameter, 12 mm | kg | 178300 | 35.2 | 6276160
47 | Diameter, 10 mm | kg | 71000 | 35.45 | 2516950
48 | Diameter, 8 mm | kg | 23835 | 35.55 | 847334.25
Concrete ancillaries
Expansion & construction Joint
49 | In 10 mm thick chip wood depth 10 cm. | m | 1400 | 34.85 | 48790
| TOTAL TO SUMMARY …………………… | BIRR |  |  | 32409805.7
04. MASONRY WORK
Stone wall
In cement mortar
01 | Concealed from view | m3 | 100 | 1261.55 | 126155
02 | Exposed face for further finish | m3 | 85 | 1305.55 | 110971.75
Dressed stone wall facing
03 | Dressed stone wall cladding on & including 20cm thick
| hcb wall externally left for pointing & internal for plastering | m2 | 305 | 641 | 195505
Concrete block works
Class "B" in cement mortar above grade walls
04 | 20 cm thick both faces for plaster | m² | 4450 | 289.7 | 1289165
05 | 15 cm thick both faces for plaster | m² | 750 | 253.7 | 190275
| TOTAL TO SUMMARY …………………… | BIRR |  |  | 1912071.75
05.ROOF WATER PROOFING & DAMP PROOFING
01 | Apply bitumen rich water proofing membrane with
4mm minimum thickness around the retaining walls,
for roof slab and concrete gutters as per the
manufacturer's instruction. Special attention shall
be given or the material shall conform to the quality
requirement of BS or other equivalent institution.
The construction shall be carried out by the supplier
of material with a certified person & will give
construction guarantee to the client. All in accordance
| with the manufacturer's details and instructions. | m² | 1900 | 282.55 | 536845
02 | Average 15cm thick light weight concrete (on roof slab) | m² | 1900 | 240.05 | 456095
03 | 3cm thick cement sand screed on light weight concrete | m² | 1900 | 101 | 191900
04 | Apply cementious water proofing material which |  |  |  | 0
shall seal void by crystallization for upper floor
wet areas (toilet rooms) to a height of 50cm on
walls and columns, as per the manufacturer's
instruction. Special attention shall be given or the
material shall conform to the quality requirement
of BS or other equivalent institution.
The cost shall include cleaning of all dirts, trace
of grease, oil and loose particles. The work shall
be done on sub contractual bases with the supplier
of the material which will give material and
| construction guarantee to the client. | m² | 300 | 222.3 | 66690
| TOTAL TO SUMMARY …………………… | BIRR |  |  | 1251530
06.ROOFING & WALL CLADDING
polycarbonate sky light
01 | Sky light alumnium framed 12mm thick multi cell
polycarbonate sheet UV value 1.84
& complete work with all its accessories
| All according to the manufacturer instruction | m² | 225 | 3919.55 | 881898.75
Ditto but doom shape
02 | dia=3.5m | Nº | 14 | 86230.3 | 1207224.2
| TOTAL TO SUMMARY …………………… | BIRR |  |  | 2089122.95
07. JOINERY
01 | Suspended Acoustic ceiling (on concrete ceiling area)
Comply EN/ASTM international standard
complete work with suspension material
a) sound absorption (0.60)
b) sound attenuation (34)
c) light reflectance (83)
| d) humidity resistance (95) | m² | 8652 | 368 | 3183936
Joinery
02 | Soffit nailed to support
| PVC ceiling for wc area | m² | 210 | 385.85 | 81028.5
| TOTAL TO SUMMARY …………………… | BIRR |  |  | 3264964.5
10. ALUMINIUM WORK
Alumiunium framed windows , window doors &
curtain wall price includes glazing .
(6mm thick black tinted glass for curtain wall & 5mm thick
clear glass for doors, windows & window doors)
_ All accessories shall be best quality and full fill
ASTM / EN quality standard requirement & to be
approved by designer prior to fixing .
_ Thickness of aluminum profiles should be
2mm thick and plate should be 3 mm thick
_ Anodization thickness should be 15-20 micro
meter price includes all accessories
locks, hinges etc…
locks shall be mortice type with standard double
cylinder & comply with quality standard
All complete work according to detail AR-21/26&22/26
Curtain wall
Curtain wall Semi structural double glassed
made of 3mm thick alloy section
Partly 5mm thick white melamine board & partly glazed
all according to drawing & given notes on the drawing
01 | Type CW1a,b,c size :-1500x1713+3712x417 cm | Nº | 1 | 1660677.7 | 1660677.7
02 | Type CW2 size :-360x1713 cm | Nº | 1 | 248726.3 | 248726.3
03 | Type CW3 size :-1900x1713 cm | Nº | 1 | 1312722.2 | 1312722.2
04 | Type CW4 size :-550x1713 cm | Nº | 1 | 379998.55 | 379998.55
05 | Type CW5 size :-245x1713 cm | Nº | 1 | 169272.1 | 169272.1
06 | Type CW6 size :-170x1713 cm | Nº | 1 | 117454.1 | 117454.1
07 | Type CW7 size :-167x1713 cm | Nº | 2 | 115381.35 | 230762.7
08 | Type CW8 size :-160x1713 cm | Nº | 1 | 110545.05 | 110545.05
09 | Type CW9 size :-1200x849 cm | Nº | 1 | 410913.9 | 410913.9
10 | Type CW10 size :-195x715 cm (over all size) | Nº | 6 | 56234.45 | 337406.7
11 | Type CW11 size :-195x849 cm | Nº | 1 | 66773.5 | 66773.5
12 | Type CW12 size :-1970x849 cm | Nº | 1 | 677665.45 | 677665.45
13 | Type CW13 size :-185x715 cm (over all size) | Nº | 14 | 53350.65 | 746909.1
14 | Type CW14 size :-160x849 cm | Nº | 6 | 54788.5 | 328731
15 | Type CW15 size :-70x849 cm | Nº | 2 | 23970 | 47940
Windows
16 | Type W1 size :-180x80 cm | Nº | 9 | 3081.8 | 27736.2
17 | Type W2 size :-200x417 cm | Nº | 2 | 17848.65 | 35697.3
18 | Type W3 size :-680x417 cm | Nº | 9 | 60685.4 | 546168.6
19 | Type W4 size :-586x417 cm | Nº | 1 | 52296.5 | 52296.5
20 | Type W5 size :-200x80 cm | Nº | 8 | 3424.2 | 27393.6
21 | Type W6 size :-730x417 cm | Nº | 7 | 65147.55 | 456032.85
22 | Type W7 size :-333x417 cm | Nº | 11 | 29718 | 326898
23 | Type W8 size :-440x417 cm | Nº | 6 | 39267 | 235602
24 | Type W9a size :-700x250 cm | Nº | 3 | 37452.2 | 112356.6
25 | Type W9b size :-680x250 cm | Nº | 3 | 36382.15 | 109146.45
Window doors
26 | Type WD1 size :-680x417 cm | Nº | 1 | 60685.4 | 60685.4
27 | Type WD2 size :-490x417 cm | Nº | 2 | 43729.15 | 87458.3
28 | Type WD3 size :-360x417 cm | Nº | 10 | 32127.55 | 321275.5
Glass luverd window ( roof level)
29 | size :-2300x110 cm | Nº | 1 | 49980.15 | 49980.15
30 | size :-3600x58 cm | Nº | 1 | 44685.8 | 44685.8
Doors
31 | Type D1 size :-90x210 cm | Nº | 31 | 4096.7 | 126997.7
32 | Type D2 size :-120x240 cm | Nº | 14 | 6242.6 | 87396.4
33 | Type D4 size :-160x240 cm | Nº | 10 | 8323.45 | 83234.5
PVC doors
34 | Type D3 size :-70x210 cm | Nº | 38 | 2823.3 | 107285.4
Alumiunium stair case hand rail & Baluster
Complete all according to drawing
35 | fixed on steps H= 90cm | m | 30 | 2524.25 | 75727.5
36 | On wall H= 30cm | m | 65 | 1975.5 | 128407.5
Alumiunium guard rail & Baluster
Complete all according to drawing
37 | H=50cm (on HCB baluster ) | m | 101 | 1975.5 | 199525.5
38 | H=90cm | m | 35 | 2414.5 | 84507.5
alum guard rail ( for stair case)
39 | Complete work all according to drawing | m² | 115 | 2804.7 | 322540.5
alum sun breaker
- Ø70mm thick vertical aluminium member placed at c/c 1000mm
- Ø70mm thick horizontal aluminium member placed at c/c 200mm
Complete all according to drawing
40 | H=100cm | m | 151 | 2414.5 | 364589.5
Corner protection
41 | In angle iron size 30x30x3mm | m | 164 | 115 | 18860
| TOTAL TO SUMMARY………… | BIRR |  |  | 10938983.6
| 11. FINISHING |  |  |  | 0
11.1 PLASTERING & POINTING
Two coats of plaster
In cement mortar to internal surface of :-
01 | Hollow concrete block wall | m² | 9060 | 120.1 | 1088106
02 | Concrete vertical surface | m² | 6625 | 123.95 | 821168.75
03 | Concrete soffit (only stair belly) | m² | 391 | 126.4 | 49422.4
In cement mortar to external surface of :-
04 | Hollow concrete block wall | m² | 1050 | 127.55 | 133927.5
05 | Concrete vertical surface | m² | 1607 | 130.75 | 210115.25
Gypsum plaster to:-
06 | Internal plastered vertical surface | m² | 14800 | 42.75 | 632700
07 | Plastered soffit (only stair belly) | m² | 391 | 43.55 | 17028.05
Fine coat cement plaster to:-
08 | Internal plastered vertical surface ( for wet area) | m² | 297 | 52.9 | 15711.3
| TOTAL TO SUMMARY …………………… | BIRR |  |  | 2968179.25
| 11.2 FLOOR & WALL FINISH |  |  |  | 0
| External wall cladding |  |  |  | 0
| Roughly textured rumic tile |  |  |  | 0
01 | Roughly textured rumic tile cladding to external plastered |  |  |  | 0
| wall surface with maxyfix approved type |  |  |  | 0
| backing or equivalent | m2 | 2660 | 463.5 | 1232910
Ceramic wall tile
02 | 6 mm thick | m² | 595 | 402.35 | 239398.25
Cement Screed floor finish & skirting
03 | 48 mm thick cement screed smooth finish
| under pvc roll. | m² | 4515 | 139.3 | 628939.5
PVC ROLL flooring and skirting
Shall be in compliance with (BS 3261) quality
standard
04 | 3 mm thick | m² | 4515 | 351.4 | 1586571
05 | 10cm high Skirting | m | 753 | 37.9 | 28538.7
Porcelain tile flooring & skirting
Porcelain tile Shall be in compliance with
ES C.D2,003 Ethiopian standard
06 | 10mm thick | m² | 3337 | 610.55 | 2037405.35
07 | Porcelain skirting | m | 1178 | 115.05 | 135528.9
Granite tile flooring & skirting
All granite tile Shall be in compliance with
ES C.D2,003 Ethiopian standard
08 | 2cm thick | m² | 976 | 2209.8 | 2156764.8
09 | Size:- 10 x 2 cm skirting | m | 85 | 283.05 | 24059.25
Non slippery Ceramic floor tile
10 | 9mm thick | m² | 207 | 559.1 | 115733.7
11 | Ceramic skirting | m | 51 | 102.65 | 5235.15
All white marble Shall be in compliance with
ES C.D2,003 Ethiopian standard
Marble tile landing & skirting
12 | 2cm thick | m² | 106 | 1342.3 | 142283.8
13 | Size:- 10 x 2 cm skirting | m | 162 | 215.8 | 34959.6
Cill and Threshold holder
Shaped and throated White marble
tile window cill and door threshold.
14 | Size:- 3x29cm | m | 489 | 463.5 | 226651.5
White marble copping
15 | Size :- 3x26 cm marble | m | 146 | 401.85 | 58670.1
Steps
Thread
16 | 3cm thick marble white | m² | 188 | 1699.5 | 319506
Riser
17 | 2cm thick marble black | m² | 100 | 2024 | 202400
pavement
included on site work
| TOTAL TO SUMMARY …………………… | BIRR |  |  | 9175555.6
| 12. PAINTING |  |  |  | 0
| Plastic Emulsion paint to :- |  |  |  | 0
01 | Internal plastered vertical surface | m² | 14800 | 33.5 | 495800
02 | Plastered soffit surface (only stair belly) | m² | 391 | 35.35 | 13821.85
Synthetic paint
03 | Internal plastered vertical surface (wet area) | m² | 296 | 40.05 | 11854.8
| TOTAL TO SUMMARY …………………… | BIRR |  |  | 521476.65
14. SANITARY INSTALLATION
All fixtures which specified below is subjected to
the consultant approval, based on samples,
catalogues, brochures presented by the contractor.
All sanitary appliances shall be best quality and
European made.
Hand Wash Basin
01 | Supply and fix European made Hand Wash Basin,
made of white vitreous China (BS3402),with pedestal.
The fixture shall conform to BS5506-3 or equivalent
institution. The mixing faucets, waste drain holes,
chrome plated angle valve, waste fittings, connecting
pieces, fixing and supporting elements and all other
accessories shall comply with the relevant clauses of
BS standard or equivalent institution.
| Size:- 600 x 500mm | No | 32 | 1121.25 | 35880
Water Closet
02 | Supply and fix European made Water closet with low
flush cistern made of enameled cast iron. The waste
fittings, connecting pieces, fixing and supporting
elements and other accessories which complete the set
shall comply with the relevant clauses of BS
| Standard or equivalent institution. | No | 32 | 2392 | 76544
Urinal
03 | Supply and fix wall hanged urinals, made of white
vitreous china which comply with requirement of
BS3402 standard or equivalent institution, complete
with flushing valve at top spud, smell trap, stainless
| steel strainer and all the necessary accessories. | No | 8 | 971.75 | 7774
Toilet Paper Holder
04 | Supply and fix European made toilet paper holder,
made of white vitreous china(BS3402) approved
| quality complete with all the necessary accessories. | No | 32 | 373.75 | 11960
Crystal Glass Mirror
05 | Supply and fix approved quality frameless crystal
glass mirror, back-silvered, minimum 6mm thick,
Size: 500mm x 400mm. Complete with theft resistant
| concealed wall fastening fittings and other accessories. | No | 32 | 598 | 19136
06 | Fire Extinguisher
Supply and fix 6kg Dry powder fire extinguisher
for ABCE class of fire, complete with approved
standard hanging and fixing materials.
Unit price shall include all the necessary assistances
| to the installation works. | No | 25 | 1495 | 37375
Water Supply Pipes
07 | Supply, lay and connect 25 mm outer diameter(OD)
PPR(PN20) pipes, for cold & hot water supply system,
complete with all the necessary connecting pieces such
as bends,Ts,reducers,adaptors,unions,sockets,hangers
(every 60cm ) & supporters (if any) etc…
Unit price shall include all the necessary assistance to
the installation works. The installation shall be tested
| at a pressure of 16kgf/cm2. | ml | 79 | 59.8 | 4724.2
08 | Ditto Item No 07 but 32mm OD | ml | 21 | 85.2 | 1789.2
09 | Ditto Item No 07 but 40mm OD | ml | 43 | 92.7 | 3986.1
10 | Supply, lay, test and commission 40mm HDPE water
supply pipe having PN16 for external water supply
system, complete with all the necessary connecting
pieces such as bends, unions, Ts ,reducers, adaptors,
sockets, hangers(every 60cm ), supporters, etc…
The installation shall be tested at a pressure of
10kg/cm2 .The Pipes and fittings shall conform to
BS6347/DIN8047 or equivalent institution.
The product quality assurance certificate has to be
| submitted along with the material for approval. | ml | 34 | 104.65 | 3558.1
Gate Valve
11 | Supply and fix bronze gate valves (PN 16) internal
diameter 25mm, of approved standards, compatible
to PP-R pipes, complete with all the necessary
| accessories. | Nº | 8 | 552 | 4416
12 | Ditto Item No 11 but 32 mm ID | Nº | 6 | 672.75 | 4036.5
13 | Ditto Item No 11 but 40mm ID | Nº | 5 | 867.1 | 4335.5
Water Tank
14 | Supply and fix 5m3 Fiber Glass Water Tank for
potable water, internally smoothen and externally
well finished, which include :-
Inlet diameter-40mm;
Outlet diameter-40mm;
Over flow diameter-40mm;
Drain diameter-40mm;
Vent pipe diameter-100mm;
Inspection manhole-600 x 600 mm;
Unit price shall include all the necessary works
| there to. | Nº | 1 | 18986.5 | 18986.5
Waste Water Drainage Pipes
15 | Supply, lay and connect 50mm diameter uPVC(PN-6)
pipes minimum wall thickness 1.88 mm for foul water
collection and drainage system, complete with all the
necessary connecting pieces such as bends,Ys,reducers,
including vent cap and vent pipe. All exposed pipes shall
be painted with UV reflective oil paint, similar to the
walls, slabs, beams…etc, complete with all necessary
fittings and clean out. The pipes, accessories, fittings
& method of welding comply to BS 5481 or equivalent
Institution. Provide galvanized clips at every 1.0m
where is necessary. Unit price shall include all the
| necessary assistance to the installation works. | ml | 84 | 134.55 | 11302.2
16 | Ditto Item No 15 but 110 mm diameter and 3.2mm
| wall thickness | ml | 139 | 224.25 | 31170.75
STORM WATER DRAINAGE SYSTEM
Down Pipes
17 | Supply and fix Diameter 110mm Upvc (PN-6) min.
wall thickness 3.2mm Downpipes with mass concrete
support at ground level & complete with UV reflective
oil painting, basket strainer at inlet, galvanized clamps
at every 1.0 meters interval and all necessary
| accessories. | ml | 323 | 228.75 | 73886.25
Waste Manhole
Size:-(600*600)mm( Av.depth 600 -1000mm )
18 | Construct rectangular manhole out of 250mm
R.C concrete C-25 walls internal dimension
(600*600)mm & average depth (600-1000mm) on a
base of R.C.slab, size,1700x1700x300mm,
including benching and bottom channeling
with mass concrete. Cover slab shall be 100mm
thick R.C. concrete reinforced with 12mm R.bar
110mm c/c and bottom slab shall be reinforced
with 10mm reinforcement bar c/c 150mm. and
250mm thick walls are reinforced with 12mm
R.bar c/c180mm in both ways. Provide 150mm
granular materials under the base slab, on a
compacted earth. manhole cover shall be
reinforced with 10mm R.bar 150mmc/c, and
shall have Ø12mm bar handle.
Unit price shall include excavation of the pit and
cart away of the excavated soil, all in accordance
| with the given detail drawing. | Nº | 6 | 17342 | 104052
Sub-Surface Pipe
19 | Supply and lay half perforated uPVC pipes
diameter 160mm with min.wall thickness 4.9mm
and 8mm hole at an angle of 22.50 laterally and
at 100 mm c/c longitudinally for withdrawal of ground
water at an average depth of 3000mm near to
the retaining wall complete with all the necessary
accessories. The pipe shall be installed beneath
selected back fill and three layers of granular
materials. Selected material thickness 1000mm ,
first layer granular material 1000mm thick with
gravel size of 10-20mm;second layer 1000mm
thick with gravel size of 20-40mm and third layer
1000mm thick with gravel size of 40-60mm.
ARRIGONI-2496 VE FRANGIVISITA
Geotextile membrane shall be installed on the
side slope of the retaining wall and beneath the
selected material
The blind part of the pipe shall be installed over
150mm thick mass concrete(C-15)and compacted
materials as shown on the given detail drawings.
The pipes,accessories,fittings and method of
welding shall comply with the requirements of
BS standard or equivalent Institution.
Unit price shall include the three layer granular
material and all the necessary assistance
to installation works and excavation of the trench
| and cart away of the excavated soil. | ml | 197 | 642.85 | 126641.45
| Selected material fill (1m thick) | ml | 197 | 65.1 | 12824.7
| 10-20mm gravel (1m thick) | ml | 197 | 404.65 | 79716.05
| 20-40mm gravel (1m thick) | ml | 197 | 703.65 | 138619.05
Sub-Surface Manhole
Size1400mm x 900mm. Depth (2500mm-5000mm)
20 | Construct rectangular manhole out of 200mm
R.C concrete C-30 walls internal dimension
1400x900 x2900mm(average depth) on a base
of R.C.slab, size,1800x1300x200mm, including benching and
bottom channeling with mass concrete. Cover slab shall be
150mm thick R.C. concrete reinforced with 8mm R.bar
150mm c/c and bottom slab shall be reinforced with
10mm reinforcement bar c/c 150mm and 200mm thick walls
are reinforced with 12mm R.bar c/c140mm in both ways.
Provide 150mm granular materials under the base
slab, on a compacted earth.
Manhole shall have cast iron cover of diameter and
thickness 650 and 270mm respectively, with a frame
of 1000mm diameter, all in accordance with the
given detail drawings. Unit price shall include
excavation of the pit to a depth of 3251 mm (Average)
and cart away of the excavated soil, all as shown
on the detail drawing.
Unit price shall include cleaning of dirt's trace of
greace,dust,oil,loose particles including any and all
| incidental works there. | Nº | 1 | 56295.7 | 56295.7
| TOTAL TO SUMMARY …………………… | BIRR |  |  | 869009.25
14.1 HVAC INSTALLATION
1 | Supply and install packaged air cooled chiller as shown on the
drawing. It includes scroll compressor, evaporator, condenser
and fan, refrigerant circuit, water side piping, hydronic module
(Isolating valve, Automatic air vent, water tank, expansion
vessel, safety valve, Ball valve, strainer, twin pump, balancing
valve, LWT senser, RWT senser, Electronic flow control ,
piping and piping ancilaries, gages etc) control panel, micro-
processor based control system and make-up water plant
(Fiberglass tank, Electric actuated valve, centrifugal pump,
check valve, isolating valve, strainer.. etc)
price shall include all accessories to make the system complete
Cooling Capacity = 115Kw at 35ºC ambient
Altitude = 2100 meters
Evaporator leaving temperature [LWT] = 7ºC
Evaporator entering temperature [RWT] = 12ºC
Refrigerant - R-407
Power supply - 380V/3Ph/ 50Hz/60 kw
size - 2700mm L /2300mm W/ 1790mm H
weight-1800 Kg
options
The pump static pressure shall be verified and determined
by the supplier
| chiller shall be acoustically lined | pcs | 3 | 1002503.65 | 3007510.95
2 | ditto item No-1 but
Cooling Capacity = 102Kw at 38ºC ambient
Power supply - 380V/3Ph/ 50Hz/55 kw
Size - 2500mm L /2000mm W/ 1695mm H
| weight-1500 Kg | pcs | 2 | 1002503.65 | 2005007.3
3 | Supply and install ceiling mounted ducted indoor fan coil with
electrical heater for straight duct arrangement as per the
drawing.(FCU-1). The unit should equipped with modulatig
3-way valve, grille volume control damper, drainage pump and
fixing accessories, 5-speed centrifugal fan, air discharged on four
sides, washable eu-2 filters, fresh air spigot dia 150mm, 150mm
flexible aluminium duct mini drainage pipe. price shall include all
accessories to make the system complete.
Type- ducted type, high static pressure
Power supply - 380V/3Ph/ 50Hz/200w
fan coil shall be acoustically lined
-Cooling capacity at 26oC DB indoor air temperature and
7ºC chilled water inlet temperature with Δt 5ºC
- 14 kw (at optimum speed)
- No of fan speed - 5
- Water pressure drop - 110kpa
- External static pressure - 130pa
- Sound pressure < 48db
- Electric power consumption ≤ 200wat
- Power supply - 230V 50HZ
The unit should include wall mounted type proportional
control panel with electronic ambient thermostat,
appropriate plenum box at discharge &suction side
kits comprising motorized three way valve, union,
kits for under ceiling installation, condensation
drip tray, condensate drainage pipe, condensate drainage pump
variable volume control damper and other accessories to
| make the system functional. | pcs | 14 | 58409.65 | 817735.1
4 | ditto item no 3, but (FCU-2)
-Cooling capacity at 26oC DB indoor air temperature and
7ºC chilled water inlet temperature with Δt 5ºC
- 10 kw (at optimum speed)
- No fan speed - 5
- Water pressure drop - 110kpa
- External static pressure - 100pa
- Sound pressure < 48db
- Electric power consumption ≤ 200wat
| - Power supply - 230V 50HZ | pcs | 16 | 46288.2 | 740611.2
5 | ditto item no 3, but (FCU-3)
-Cooling capacity at 26oC DB indoor air temperature and
7ºC chilled water inlet temperature with Δt 5ºC
- 12 kw (at optimum speed)
- Water pressure drop - 110kpa
- External static pressure - 100pa
- Sound pressure < 48db
- Electric power consumption ≤ 200wat
| - Power supply - 230V 50HZ | pcs | 13 | 54373.9 | 706860.7
6 | Supply and install GS pipe with schedule number 40 as
shown on the drawing. Price shall include hangers, shut- off
valves, flexible connection, gages, insulation, regulating valves,
non return valves, strainer, vent, automatic control valves
fittings (elbow, fees, yees) and all accessories to complete the
air- water system.
Heat insulation
Type- closed cell rubber tube insulation.
For concealed piping
- 25 mm x 48 kg/m3 insulation, vapour barrier and adhesive
tape covering
For exposed piping
- 50 mm x 48kg/m3 insulation , vapour barrier and 0.4mm
aluminum cladding.
pipe size (mm)
| DN 125 | lm | 40 | 1316.65 | 52666
| DN 100 | lm | 70 | 1227.4 | 85918
| DN 80 | lm | 120 | 1060.7 | 127284
| DN 65 | lm | 140 | 929.9 | 130186
| DN 50 | lm | 140 | 789.35 | 110509
| DN 40 | lm | 225 | 722.1 | 162472.5
| DN 32 | lm | 350 | 524.75 | 183662.5
7 | supply and install ball valve with PN 16 for chilled water
system at the branch of each floor as shown on the drawing
complete with all fixing accessories.
Valve size (mm)
| DN 125 | pcs | 2 | 12880.9 | 25761.8
| DN 100 | pcs | 4 | 11307.45 | 45229.8
| DN 80 | pcs | 14 | 6947.25 | 97261.5
| DN 65 | pcs | 8 | 5935.15 | 47481.2
8 | supply and install double regulating valve with PN 16 for
chilled water system at the branch of each floor as shown on
the drawing complete with all fixing accessories.
Valve size (mm)
| DN 125 | pcs | 2 | 12880.9 | 25761.8
| DN 100 | pcs | 4 | 11307.45 | 45229.8
| DN 80 | pcs | 14 | 6974.25 | 97639.5
| DN 65 | pcs | 8 | 5935.15 | 47481.2
9 | Supply and install hard pvc drainage pipe for fan coil
as shown on the drawing and complete with all accessories.
| all drainage must be to the nearest sanitary | ls | 1 | 36552.75 | 36552.75
10 | Supply and install centrifugal box s-proof fresh air supply fan as
shown on the drawing complete with multi-speed switch,
appropriate filter back draught shutter, spigot, sound attenuator
and all fixing accessories including support base..
price shall include all accessories to make the system complete
Purpose- fresh air supply for library
Type: Box type centrifugal box fan
Extraction capacity = 1320 lps
Total static pressure= 45 mm H20
| Power supply - 3kw/ 230V/ 50HZ | pcs | 1 | 78711.75 | 78711.75
Extraction capacity = 1260 lps
Total static pressure= 45 mm H20
| Power supply - 3kw/ 230V/ 50HZ | pcs | 1 | 77307.2 | 77307.2
Extraction capacity = 1218 lps
Total static pressure= 45 mm H20
| Power supply - 3kw/ 230V/ 50HZ | pcs | 3 | 76485.7 | 229457.1
Extraction capacity = 600 lps
Total static pressure= 320 mm H20
| Power supply - 1.0kw/ 230V/ 50HZ | pcs | 1 | 32493.85 | 32493.85
11 | Supply and install pressure relief dumper with pressure senseor,
flow regulator damper, metallic protective cabinet with rust
proof polyester paint, control system and all its accessories
to make the system complete.
Size
400 x 300 mm
| Flow: 334 lps | pcs | 16 | 21992.2 | 351875.2
12 | Supply and install galvanized steel sheet for supply duct
system as shown on the drawing complete with insulation, flexible
duct, transition duct, hangers and supports, silencer vibration
isolator, damper, turning and splitter vanes at each fitting,
stiffener, flanges
Insulation
For concealed duct
- 15mm x 48kg/m3 k = 0.033 w/mk fiber glass insulation,
vapour barrier and adhesive tape covering.
For exposed duct
- 25mm x 48kg/m3 k = 0.033 w/mk fiber glass insulation,
vapour barrier and 0.4mm aluminum cladding
Duct thickness 0.8mm
| Total sheet metal | m² | 850 | 1158.65 | 984852.5
13 | Supply and install volume control damper as shown on the
drawing complete with all fixing accessories.
Size
| 250x225mm | pcs | 18 | 1191.5 | 21447
| 200x125mm | pcs | 24 | 988.2 | 23716.8
| 150x125mm | pcs | 2 | 852.15 | 1704.3
14 | Supply and install return linear slot diffuser (RLSD) which is
made from high quality extruded alluminium profile with register
as shown on the drawing complete with dust filter and all fixing
accessories to make the system complete.
Size: 1000x200mm
(RLSD)
face velocity: 3.5m/s
| flow: 0.505m³/s | pcs | 86 | 5045.65 | 433925.9
15 | Supply and install supply linear slot diffuser (SLSD) which is
made from high quality extruded alluminium profile with register
as shown on the drawing complete with dust filter and all fixing
accessories to make the system complete.
Size: 1000x200mm
(SLSD)
face velocity: 3.5m/s
| flow: 0.505m³/s | pcs | 86 | 5867.9 | 504639.4
Toilet
16 | Supply and install centrifugal box s-proof extraction fan
as shown on the drawing complete with multi-speed switch,
metallic filter back draught shutter, spigot, sound attenuator and
all fixing accessories including odour filter.
price shall include all accessories to make the system complete
Purpose: toilet exaust ventilation
Extraction capacity = 700 lps
| Total static pressure= 48 mm H20 | pcs | 1 | 70448.9 | 70448.9
17 | Supply and install exaust air defuser with register one fixed
blade the other adjustable as shown on the drawing complete
with dust filter damper and all fixing accessories
Size
| 200x200 mm (ED) | pcs | 28 | 1113.8 | 31186.4
18 | Supply and install volume control damper as shown on the
drawing complete with all fixing accessories.
Size
| 250x200mm | pcs | 4 | 1151.15 | 4604.6
| 150x150mm | pcs | 8 | 926.9 | 7415.2
19 | Supply and install galvanized steel sheet for toilet exhaust duct
system as shown on the drawing complete with flexible duct,
transition duct, hangers and supports, silencer vibration isolator,
damper, turning and splitter vanes at each fitting, stiffener,
flanges
Duct thickness 0.8mm
| Total sheet metal | m² | 120 | 784.9 | 94188
20 | Supply and install aluminum flexible duct as shown on
the drawing complete with plenium box and all fixing accessories.
Size
| 125mm | lm | 30 | 215.3 | 6459
Server room
21 | Supply, install & commissions split close control air conditioning
equipment for serve rand UPS rooms consisting of scroll
compressor, condensing unit and Evaporating unit complete with
all accessories including filters and appropriate humidifier.
Type- floor standing close control unit
Function- cool,heat,humidify and dehumidify
Air flow direction - down ward
Cooling capacity - 18 kw at +35ºC
Heating capacity - 8 kw at +7ºC
power input- 220v/5kw/50Hz/1ph
Refrigerate type - R407c
Accessories
- Refrigerators lines including : Copper pipes for liquid and
suction lines, fittings, suction line insulation, glue and tape
for insulation joints, rubber clad pipe clamps and fixing
rods, pipe sleeve.
- Drain line including - armoured pvc hose, hose connection,
pipe sleeve & pipe clamps.
- Provide out door condensing unit cover and support
- PLC (Programable Logic Controller) with digital display
- Protection facilities - HP/LP cut out over load temp.,
| Alarm and fan delay | pcs | 1 | 402977.25 | 402977.25
| TOTAL TO SUMMARY …………………… | BIRR |  |  | 11956232.95
15. ELECTRICAL WORKS
SUPPLY AND INSTALL
Distribution boards
All boards shall be wired and tested as relevant IEC standards
1 | A.Floor standing metal enclousures type tested Central
main distribution board MDB-1 factory built, inclu
ding busbars of 1500 rating & 50KA/1sec, all other
connecting and fixing accessories for busway system ,
all tested and wired to relevant IEC standard, and consisting of:-
1pc main MCCB of 1250A, 3ph, 4 pole Icu= 50KA
3pc MCB of 63A, 3ph, Icu=16KA.
1pc MCCB of 80A, 3ph, Icu= 16KA.
4Pcs MCB of 50A, 3ph, 1cu=10KA.
1Pcs MCB of 32A, 3ph, 1cu=10KA.
1Pcs MCCB of 250A, 3ph, 1cu=36KA.
1Pcs MCCB of 160A, 3ph, 1cu=36KA.
1Pcs MDB-U of 300A, 3ph, 1cu=36KA.
3Pcs ammeters: 0-1500A
3Pcs current transformers: 1500/5A
1pc Voltmeter with selector switch
1pc frequency mete and power factor
1pc digital KWH meter for incoming supply
1pc digital data logger unit for all electrical
parameters including harmonics
1pc factory made drawing pocket, Himel PP-A4
equivalent. use DIN rail mounted terminal blocks
with end brackets and marking tags for all outgoings.
| all complete with 30% reserve spaces. | Nº | 1 | 142025 | 142025
B.Flush mounted distribution board, but for SDB-BL, IP54,
made of steel with lockable door including earthing
lead, front cover all fixing and connection accessories,
complete and consisting of:-
1pc main MCB of 63A, 3ph, 3 pole Icu= 16KA
3pcs MCB of 10A, 1ph , Icu=6KA
8pcs MCB of 16A, 1ph , Icu=6KA
1pcs MCB of 25A, 1ph, Icu=6KA
1 pcs MCB of 50A, 3ph/3pole , Icu=10KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4
or equivalent.
all complete with phase bar system of 80A and 25%
| reserve spaces. | Nº | 1 | 4893.15 | 4893.15
C.Dito, but for SDB-BR and consisting of:-
1pc main MCB of 50A, 3ph, 3 pole Icu= 10KA
7pcs MCB of 10A, 1ph , Icu=6KA
14pcs MCB of 16A, 1ph , Icu=6KA
1pcs MCB of 25A, 1ph, Icu=6KA
1 pcs MCB of 16A, 3ph/3pole , Icu=10KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4 or equivalent.
all complete with phase bar system of 63A and 25%
| reserve spaces. | Nº | 1 | 3737.5 | 3737.5
2 | A. Flush mounted distribution board, but for SDB-GFL,IP54,
made of steel with lockable door including earthing
lead, front cover all fixing and connection accessories,
complete and consisting of:-
1pc main MCB of 63A, 3ph, 3 pole Icu= 16KA
9pcs MCB of 10A, 1ph , Icu=6KA
8pcs MCB of 16A, 1ph , Icu=6KA
1pcs MCB of 16A,3ph/3pole, Icu=10KA
1 pcs MCB of 50A, 3ph/3pole , Icu=10KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4
or equivalent.
all complete with phase bar system of 80A and 25%
| reserve spaces. | Nº | 1 | 3921.4 | 3921.4
B. Dito but for SDB-GFR and consisting of:-
1pc main MCB of 50A, 3ph, 3 pole Icu= 10KA
6pcs MCB of 10A, 1ph , Icu=6KA
5pcs MCB of 16A, 1ph , Icu=6KA
1pcs MCB of 25A,3ph/3pole, Icu=10KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4
or equivalent.
all complete with phase bar system of 63A and 25%
| reserve spaces. | Nº | 1 | 3102.15 | 3102.15
B-1. Dito but for DB-GFR and consisting of:-
1pc main MCB of 25A, 3ph, 3 pole Icu= 10KA
6pcs MCB of 10A, 1ph , Icu=6KA
6pcs MCB of 16A, 1ph , Icu=6KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4 or equivalent.
all complete with phase bar system of 32A and 25%
| reserve spaces. | Nº | 1 | 2754.55 | 2754.55
3 | A. Flush mounted distribution board, but for SDB-1FL, IP54,
made of steel with lockable door including earthing
lead, front cover all fixing and connection accessories,
complete and consisting of:-
1pc main MCB of 63A, 3ph, 3 pole Icu= 16KA
3pcs MCB of 10A, 1ph , Icu=6KA
14pcs MCB of 16A, 1ph , Icu=6KA
1pcs MCB of 32A,3ph/3pole, Icu=10KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4
or equivalent.
all complete with phase bar system of 80A and 25%
| reserve spaces. | Nº | 1 | 4111.25 | 4111.25
B. Dito but for SDB-1FR and consisting of:-
1pc main MCB of 32A, 3ph, 3 pole Icu= 10KA
2pcs MCB of 10A, 1ph , Icu=6KA
1pcs MCB of 16A, 1ph , Icu=6KA
1pcs MCB of 25A,3ph/3pole, Icu=10KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4
or equivalent.
all complete with phase bar system of 50A and 25%
| reserve spaces. | Nº | 1 | 2137.85 | 2137.85
B-1. Dito but for DB-1FR and consisting of:-
1pc main MCB of 25A, 3ph, 3 pole Icu= 10KA
2pcs MCB of 10A, 1ph , Icu=6KA
10pcs MCB of 16A, 1ph , Icu=6KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4 or equivalent.
all complete with phase bar system of 32A and 25%
| reserve spaces. | Nº | 1 | 3001.2 | 3001.2
4 | A. Flush mounted distribution board, but for SDB-2FL ,IP54,
made of steel with lockable door including earthing
lead, front cover all fixing and connection accessories,
complete and consisting of:-
1pc main MCCB of 80A, 3ph, 3 pole Icu= 16KA
3pcs MCB of 10A, 1ph , Icu=6KA
15pcs MCB of 16A, 1ph , Icu=6KA
1pcs MCB of50A,3ph/3pole, Icu=10KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4
or equivalent.
all complete with phase bar system of 100A and 25%
| reserve spaces. | Nº | 1 | 8633.65 | 8633.65
B. Dito, but for SDB-2FR and consisting of:-
1pc main MCB of 50A, 3ph, 3 pole Icu= 10KA
3pcs MCB of 10A, 1ph , Icu=6KA
15pcs MCB of 16A, 1ph , Icu=6KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4
or equivalent.
all complete with phase bar system of 63A and 25%
| reserve spaces. | Nº | 1 | 3371.25 | 3371.25
5 | A. Flush mounted distribution board, but for SDB-3FL ,IP54,
made of steel with lockable door including earthing
lead, front cover all fixing and connection accessories,
complete and consisting of:-
1pc main MCB of 50A, 3ph, 3 pole Icu= 10KA
2pcs MCB of 10A, 1ph , Icu=6KA
11pcs MCB of 16A, 1ph , Icu=6KA
1pcs MCB of25A,3ph/3pole, Icu=10KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4
or equivalent.
all complete with phase bar system of 63A and 25%
| reserve spaces. | Nº | 1 | 3289 | 3289
B. Dito but for SDB-3FR and consisting of:-
1pc main MCB of 25A, 3ph, 3 pole Icu= 10KA
5pcs MCB of 10A, 1ph , Icu=6KA
3pcs MCB of 16A, 1ph , Icu=6KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4
or equivalent.
all complete with phase bar system of 32A and 25%
| reserve spaces. | Nº | 1 | 2302.3 | 2302.3
6 | Flush mounted distribution board, but for SDB-LIFT ,IP54,
made of steel with lockable door including earthing
lead, front cover all fixing and connection accessories,
complete and consisting of:-
1pc main MCB of 32A, 3ph, 3 pole Icu= 10KA
1pcs MCB of 10A, 1ph , Icu=6KA
1pcs MCB of 25A, 3ph /3pole, Icu=10KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4
or equivalent.
all complete with phase bar system of 50A and 25%
| reserve spaces. | Nº | 1 | 1973.4 | 1973.4
7 | Flush mounted distribution board, but for DB-3F-AC1 ,IP54,
made of steel with lockable door including earthing
lead, front cover all fixing and connection accessories,
complete and consisting of:-
and consisting of:-
1pc main MCCB of 250A, 3ph, 3 pole Icu= 36KA
3pcs MCCB of 80A, 3ph /3pole, Icu=16KA
1pcs MCB of 10A, 3ph /3pole, Icu=10KA
2pcs MCB of 16A, 3ph /3pole, Icu=10KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4
or equivalent.
all complete with bus bar system of 300A and 25%
| reserve spaces. | Nº | 1 | 19322.9 | 19322.9
8 | Flush mounted distribution board, but for DB-3F-AC2 ,IP54,
made of steel with lockable door including earthing
lead, front cover all fixing and connection accessories,
complete and consisting of:-
1pc main MCCB of 160A, 3ph, 3 pole Icu= 36KA
4pcs MCB of 10A, 3ph /3pole, Icu=10KA
2pcs MCCB of 80A, 3ph /3pole, Icu=16KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4
or equivalent.
all complete with bus bar system of 200A and 25%
| reserve spaces. | Nº | 1 | 13978.25 | 13978.25
9 | Floor standing metal enclousures type tested
main distribution board MDB-UPS factory built,
including busbars of 355A rating & 50KA/1sec,
all other connecting and fixing accessories, all tested
and wired to relevant IEC standard, and consisting of:-
1pc main MCCB of 300A, 3ph, Icu= 20KA
15 Pcs MCB of 16A, 1ph, 1cu=6KA.
5 pc MCB of 25A, 3ph, Icu= 10KA.
2 pc MCB of 32A, 3ph, Icu= 10KA.
1pcs MCB of 80A, 3ph/3pole , Icu=16KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4
| or equivalent all complete and 25% reserve spaces. | Nº | 1 | 24955.3 | 24955.3
10 | Flush mounted distribution board, DB-B-U, IP54,
made of steel with lockable door including earthing
lead, front cover all fixing and connection accessories,
complete and consisting of:-
1pc main MCB of 32A, 3ph, 3 pole Icu= 20KA
12pcs MCB of 16A, 1ph , Icu= 6KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4
or equivalent.
all complete with bus bar system of 50A and 25%
| reserve spaces. | Nº | 1 | 2754.55 | 2754.55
11 | Flush mounted distribution board, SDB-GFR-U, IP54,
made of steel with lockable door including earthing
lead, front cover all fixing and connection accessories,
complete and consisting of:-
1pc main MCB of 32A, 3ph, 3 pole Icu= 20KA
14pcs MCB of 16A, 1ph , Icu= 6KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4
or equivalent.
all complete with bus bar system of 50A and 25%
| reserve spaces. | Nº | 1 | 3001.2 | 3001.2
12 | Flush mounted distribution board, SDB-GFL-U, IP54,
made of steel with lockable door including earthing
lead, front cover all fixing and connection accessories,
complete and consisting of:-
1pc main MCB of 25A, 3ph, 3 pole Icu= 20KA
9 pcs MCB of 16A, 1ph , Icu= 6KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4 or equivalent.
all complete with bus bar system of 50A and 25%
| reserve spaces. | Nº | 1 | 2466.75 | 2466.75
13 | Flush mounted distribution board, SDB-1FR-U, IP54,
made of steel with lockable door including earthing
lead, front cover all fixing and connection accessories,
complete and consisting of:-
1pc main MCB of 25A, 3ph, 3 pole Icu= 10KA
9 pcs MCB of 16A, 1ph , Icu= 6KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4 or equivalent.
all complete with bus bar system of 32A and 25%
| reserve spaces. | Nº | 1 | 2466.75 | 2466.75
14 | A. Flush mounted distribution board, SDB-1FL-U, IP54,
made of steel with lockable door including earthing
lead, front cover all fixing and connection accessories,
complete and consisting of:-
1pc main MCB of 32A,3ph, Icu= 10KA
8 pcs MCB of 16A, 1ph , Icu= 6KA
1 pcs MCB of 25A, 1ph , Icu= 6KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4
or equivalent.
all complete with bus bar system of 63A and 25%
| reserve spaces. | Nº | 1 | 2466.75 | 2466.75
B.Flush mounted distribution board, DB-1FL-U, IP54,
made of steel with lockable door including earthing
lead, front cover all fixing and connection accessories,
complete and consisting of:-
1pc main MCB of 25A, 1ph, Icu= 6KA
4 pcs MCB of 16A, 1ph, Icu= 6KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4
or equivalent.
all complete with bus bar system of 32A and 25%
| reserve spaces. | Nº | 1 | 1685.6 | 1685.6
15 | Flush mounted distribution board, SDB-2FR-U, IP54,
made of steel with lockable door including earthing
lead, front cover all fixing and connection accessories,
complete and consisting of:-
1pc main MCB of 25A, 3ph, 3 pole Icu= 20KA
9 pcs MCB of 16A, 1ph , Icu= 6KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4
or equivalent.
all complete with bus bar system of 32A and 25%
| reserve spaces. | Nº | 1 | 2919 | 2919
16 | A. Flush mounted distribution board, SDB-2FL-U, IP54,
made of steel with lockable door including earthing
lead, front cover all fixing and connection accessories,
complete and consisting of:-
1pc main MCB of 32A, 3ph, 3pole Icu= 10KA
4 pcs MCB of 16A, 1ph , Icu= 6KA
1 pcs MCB of 25A, 1ph , Icu= 6KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4
or equivalent.
all complete with bus bar system of 50A and 25%
| reserve spaces. | Nº | 1 | 1932.3 | 1932.3
17 | B.Flush mounted distribution board, DB-2FL-U, IP54,
made of steel with lockable door including earthing
lead, front cover all fixing and connection accessories,
complete and consisting of:-
1pc main MCB of 25A, 1ph, 1pole Icu= 10KA
4 pcs MCB of 16A, 1ph/1pole , Icu= 6KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4 or equivalent.
all complete with bus bar system of 32A and 25%
| reserve spaces. | Nº | 1 | 1932.3 | 1932.3
18 | Flush mounted distribution board, SDB-3FR-U, IP54,
made of steel with lockable door including earthing
lead, front cover all fixing and connection accessories,
complete and consisting of:-
1pc main MCCB of 80A, 3ph, 3 pole Icu= 16KA
4pcs MCB of 25A,3ph/3pole , Icu= 10KA
1pc main MCB of 25A, 1ph, Icu= 10KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4
or equivalent.
all complete with bus bar system of 100A and 25%
| reserve spaces. | Nº | 1 | 7030.25 | 7030.25
19 | Flush mounted distribution board, DB--1-U ,IP54,
made of steel with lockable door including earthing
lead, front cover all fixing and connection accessories,
complete and consisting of:-
1pc main MCB of 25A,1ph, Icu= 20KA
10 pcs MCB of 16A, 1ph , Icu= 6KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4 or equivalent.
all complete with bus bar system of 50 A and 25%
| reserve spaces. | Nº | 1 | 2466.75 | 2466.75
20 | Flush mounted distribution board, DB-2-U, IP54,
made of steel with lockable door including earthing
lead, front cover all fixing and connection accessories,
complete and consisting of:-
1pc main MCB of 25A, 3ph, 3 pole Icu= 20KA
10pcs MCB of 16A, 1ph , Icu= 6KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4 or equivalent.
all complete with bus bar system of 63A and 25%
| reserve spaces. | Nº | 1 | 2507.85 | 2507.85
21 | Flush mounted distribution board, SDB-3-U, IP54,
made of steel with lockable door including earthing
lead, front cover all fixing and connection accessories,
complete and consisting of:-
1pc main MCB of 32A, 1ph, 3pole Icu= 6KA
8 pcs MCB of 16A, 1ph/1pole , Icu= 6KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4
or equivalent.
all complete with bus bar system of 50A and 25%
| reserve spaces. | Nº | 1 | 2425.65 | 2425.65
22 | Flush mounted distribution board, SDB-4-U, IP54,
made of steel with lockable door including earthing
lead, front cover all fixing and connection accessories,
complete and consisting of:-
1pc main MCB of 25A, 3ph, 3pole Icu= 10KA
8 pcs MCB of 16A, 1ph/1pole , Icu= 6KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4 or equivalent.
all complete with bus bar system of 50A and 25%
| reserve spaces. | Nº | 1 | 2507.85 | 2507.85
23 | Flush mounted distribution board, SDB-3FL-U, IP54,
made of steel with lockable door including earthing
lead, front cover all fixing and connection accessories,
complete and consisting of:-
1pc main MCB of 25A, 1ph, 1pole Icu= 6KA
5 pcs MCB of 16A, 1ph/1pole , Icu= 6KA
use DIN rail mounted terminal blocks with
end brackets and marking tags for all outgoings.
1pc factory made drawing pocket, Himel PP-A4 or equivalent.
all complete with bus bar system of 50A and 25%
| reserve spaces. | Nº | 1 | 2343.4 | 2343.4
LIGHT POINTS
3rd party certified
24 | Light points in medium duty rigid conduit of
16mm fed by PVC insulated copper conductor of
| 2x2.5sq.mm. | Nº | 939 | 380.9 | 357665.1
SWITCHES IP54
3rd party certified
10A/1ph flush mounted with
appropriate cover plate, frame and box.
Note: use modular appropriate back box for concrete ,
masonry wall and for light or gypsum wall.
25 | 1-way | Nº | 49 | 82.25 | 4030.25
26 | Three-gang 1-way | Nº | 9 | 90.45 | 814.05
27 | 2-way | Nº | 8 | 119.25 | 954
28 | Intermediate | Nº | 2 | 138.95 | 277.9
29 | Double switch | Nº | 50 | 121.7 | 6085
SOCKET OUTLETS POWER POINTS AND FLOOR BOX
3rd party certified
Flush mounted with appropriate cover plate, frame
and box.
Note: use modular appropriate back box for concrete ,
masonry wall and for light or gypsum wall.
30 | Socket outlet flush mounted, 16A 2-gang (twin)Red
color , 1ph, schuko type in medium duty rigid
thermoplastic conduit of diameter 16mm fed by
| PVC insulated copper conductor of 3x2.5mm2. | Nº | 296 | 531.3 | 157264.8
31 | Socket outlet flush mounted, 16A 1-gang Red color
,1ph schuko type in medium duty rigid
thermoplastic conduit of diameter 16mm fed by PVC
| insulated copper cable of 3x2.5mm2. | Nº | 80 | 815.95 | 65276
Extra over
32 | Socket out lets with detachable frames & corresponding
box 3rd party certified
a | 16A,1ph TWIN for UPS with Red /or other color | Nº | 269 | 213.8 | 57512.2
b | 16A,1ph | Nº | 80 | 102.8 | 8224
Floor box
- Floor box shall be fixed neatly in contact with the
horizontal surface of the floor with the necessary fixers
or connectors with IP 54 enclousures
- Floor box ,data, socket and telephone out lets
shall be the product of the same manufacture.
33 | Approved type dual service Slim modular round
Non-Metallic Concrete Floor Box with complete
conduit accessories consisting of 4pc RJ45/8
contact cat 6 data socket outlet,2pcs pre-wired twin schuko
RED 220V receptacles over floor covers and frames .
Supplied with reusable concrete cap, conduit hub
plugs and reducers. With two hubs for low voltage
and two hubs for power. Reducers to provide reduction
of PVC conduit. Markings inside the box Universal cover
| and sub-plate | Nº | 164 | 3338.35 | 547489.4
34 | Approved type dual service Slim modular round
Non-Metallic Concrete Floor Box with complete
conduit accessories consisting of 6pc RJ45/8
contact cat 6 data socket outlet,3pcs pre-wired twin schuko
RED 220V receptacles over floor covers and frames .
Supplied with reusable concrete cap, conduit hub
plugs and reducers. With two hubs for low voltage
and two hubs for power. Reducers to provide reduction
of PVC conduit. Markings inside the box Universal cover
| and sub-plate | Nº | 6 | 4303.65 | 25821.9
35 | Approved type dual service Slim modular round
Non-Metallic Concrete Floor Box with complete
conduit accessories consisting of 2pc RJ45/8
contact cat 6 data socket outlet,1pcs pre-wired twin schuko
RED 220V receptacles over floor covers and frames .
Supplied with reusable concrete cap, conduit hub
plugs and reducers. With two hubs for low voltage
and two hubs for power. Reducers to provide reduction
of PVC conduit. Markings inside the box Universal cover
| and sub-plate | Nº | 30 | 3363 | 100890
Lift shaft lighting
36 | Lift shaft light points as manufacturer instruction
fed by PVC insulated cable of 3x2.5mm2 in medium
duty PVC conduit diameter of 20mm(From
machine room).price shall separate include isolator
| switch for each shaft | Nº | 6 | 569.25 | 3415.5
37 | Power supply for lift motor fed by PVC insulated
cable of 5x6sq.mm in medium duty PVC conduit
| diameter of 25mm(length 20m). | Nº | 1 | 4421.2 | 4421.2
Master Light control panel
39 | Semi-recessed/surface mounted microprocessor based with
Non-volatile memory that holds all programming indefinitely.
Ten-year battery back-up for time-of-day or
approved type master lighting control panel (LCP), IP54,
made of steel with lockable door 2 switch inputs,
Relay Control Card(manual control of zones or
individual relays)8 relay out puts 36-channel, 365-day
astro clock Access and program the entire system
with astromincal programmable clock, 220V AC control
voltage ,50Hz RS-485/RJ45 communication ports for 50
degree celisius and 90% humidity operation with
transformers, LED indicators for system relay
and status up to 256 digital devices ,factory programming ,
back up power supply unit,21 x 8 characters acts as the
programming interface for the entire system LCD display,
photo sensor and all the necessary accessories including DIN rail
mounted terminal blocks, end brackets, marking
| tags all fixing and connection accessories. | Nº | 1 | 168561.25 | 168561.25
40 | Ditto as above but slave with 4 relay out put and
| 4 channel | Nº | 5 | 18089.5 | 90447.5
41 | Ditto as above but slave with 6 relay out put and
| 6channel | Nº | 1 | 47690 | 47690
42 | Ditto as above but slave with 8 relay out put and
| 8 channel | Nº | 2 | 34534.5 | 69069
21 | Light control panels, installed, connected, tested
and commissioned including power, CAT 6 data cables,
subswiches,programming soft wares, conduits and all
necessary accessories , complete as manufactured and/or
shown on drawings with complete shop drawings and .
analysis made before manufacturing instillation
| and conducting | Nº | 3 | 30423.25 | 91269.75
22 | Light control panels and power panel boards,
wiring conducting including multiple pair 6x1sq.mm cables,
conduits and all necessary accessories, complete as
manufactured and/or shown on drawings with complete
shop drawings and .analysis made before manufacturing
| instillation and conducting | Nº | 2 | 26312 | 52624
23 | Light control panels and power panel boards,
wiring conducting including multiple pair10x1sq.mm cables,
conduits and all necessary accessories, complete as
manufactured and/or shown on drawings with complete
shop drawings and .analysis made before manufacturing
| instillation and conducting | Nº | 1 | 34205.6 | 34205.6
24 | Light control panels and power panel boards,
wiring conducting including multiple pair12x1sq.mm cables,
conduits and all necessary accessories, complete as
manufactured and/or shown on drawings with complete
shop drawings and .analysis made before manufacturing
| instillation and conducting | Nº | 1 | 39336.45 | 39336.45
VOICE / DATA SYSTEM
3rd party certified
Flush mounted with appropriate cover plate, frame and box.
Note: use modular appropriate back box for concrete ,
masonry wall and for light or gypsum wall.
43 | A. Twin Data points fed by cable 2x category 6 UTP
4 pair data cable inside medium duty PVC conduit
| of 20mm. Price to include CAT 6 RJ45 termination,3 | Nº | 233 | 476.9 | 111117.7
B. Data points fed by cable 4x category 6 UTP
4 pair data cable inside medium duty PVC conduit
of 29mm. Price to include CAT 6 RJ45 termination,3
| meter patch cord and all necessary accessories. | No | 124 | 435.8 | 54039.2
C. Data points fed by cable 6x category 6 UTP
4 pair data cable inside medium duty PVC conduit
of 29mm. Price to include CAT 6 RJ45 termination,3
| meter patch cord and all necessary accessories. | No | 34 | 509.8 | 17333.2
44 | Data points fed by cable 1x category 6 UTP
4 pair data cable inside medium duty PVC conduit
of 16mm. Price to include CAT 6 RJ45 termination,
| 3 meter patch cord and all necessary accessories. | No | 30 | 575.6 | 17268
45 | RJ45 twin outlets type , Category 6 with 8 contacts
| complete with all necessary accessories | No | 233 | 164.45 | 38316.85
46 | RJ45 outlets type , Category 6 with 8 contacts
| complete with all necessary accessories | No | 30 | 131.55 | 3946.5
47 | RJ45/8 contact to RJ11 4 contact convertor | Nº | 35 | 657.8 | 23023
Back bone cabling
48 | Back bone cabling for flush mounting in
thermoplastic conduit of 20mm with appropriate
type junction box fed by standard 4XCAT 6E
data cable for 10/100 base entarnet with standard
connector plug to be fixed on patch panel /switch/
hub data transfer rate of 100Mbs and the necessary
| accessories to make the system complete. | ml | 800 | 296 | 236800
Telephone Terminal Blocks(Distribution frames)
with corresponding box and frames(optional)
49 | Surface mounted 100 pairs telephone terminal
blocks(telephone distribution frame) or Punch down
blocks with plastic cover of similar color to the
| adjacent wall support structure complete accessories | Nº | 1 | 30258.8 | 30258.8
Telephone Distribution cables(optional)
50 | 20 pairs CAT 5 UTP telephone cable partly in PVC
| dia.29mm(or equivalent pair as ETC standards) | m | 233 | 98.65 | 22985.45
Patch panels
51 | A. Patch panel for PP-BF with 96 6U ports 8/4 contact
in fixed & 15U or approved equivalent swing 19"
steel enclosure with transparent and lockable door,
with corresponding power supply unit of 8pcs scuko
type socket out lets with power plug and standard
pivoting cabinet with rack for wall mounting , knock-
out holes for cable entrance and conduit connection,
ventilation ports , standard patch cords (3meters)
and 25% reserve space for hubs and switches, with
fiber to copper converter, CAT 6, including screen,
| lable holder and all the necessary accessories.. | Nº | 3 | 21378.5 | 64135.5
B.Patch panel for PP-BF with 120 5U ports 8/4 contact
in fixed & 15U or approved equivalent swing 19"
steel enclosure with transparent and lockable door,
with corresponding power supply unit of 8pcs scuko
type socket out lets with power plug and standard
pivoting cabinet with rack for wall mounting , knock-
out holes for cable entrance and conduit connection,
ventilation ports , standard patch cords (3meters)
and 25% reserve space for hubs and switches, with
fiber to copper converter, CAT 6, including screen,
| lable holder and all the necessary accessories.. | Nº | 1 | 21378.5 | 21378.5
C.Patch panel for PP-BFwith 24U ports 8/4 contact
in fixed & 15U or approved equivalent swing 19"
steel enclosure with transparent and lockable door,
with corresponding power supply unit of 8pcs scuko
type socket out lets with power plug and standard
pivoting cabinet with rack for wall mounting , knock-
out holes for cable entrance and conduit connection,
ventilation ports , standard patch cords (3meters)
and 25% reserve space for hubs and switches, with
fiber to copper converter, CAT 6, including screen,
| lable holder and all the necessary accessories.. | Nº | 1 | 9867 | 9867
D.Patch panel for PP-GF with 72 3U ports 8/4 contact
in fixed & 15U or approved equivalent swing 19"
steel enclosure with transparent and lockable door,
with corresponding power supply unit of 8pcs scuko
type socket out lets with power plug and standard
pivoting cabinet with rack for wall mounting , knock-
out holes for cable entrance and conduit connection,
ventilation ports , standard patch cords (3meters)
and 25% reserve space for hubs and switches, with
fiber to copper converter, CAT 6, including screen,
| lable holder and all the necessary accessories.. | Nº | 3 | 10689.25 | 32067.75
E.Patch panel for PP-GF with 48 2U ports 8/4 contact
in fixed & 15U or approved equivalent swing 19"
steel enclosure with transparent and lockable door,
with corresponding power supply unit of 8pcs scuko
type socket out lets with power plug and standard
pivoting cabinet with rack for wall mounting , knock-
out holes for cable entrance and conduit connection,
ventilation ports , standard patch cords (3meters)
and 25% reserve space for hubs and switches, with
fiber to copper converter, CAT 6, including screen,
| lable holder and all the necessary accessories.. | Nº | 1 | 7400.25 | 7400.25
F.Patch panel for PP-GF with 120 5U ports 8/4 contact
in fixed & 15U or approved equivalent swing 19"
steel enclosure with transparent and lockable door,
with corresponding power supply unit of 8pcs scuko
type socket out lets with power plug and standard
pivoting cabinet with rack for wall mounting , knock-
out holes for cable entrance and conduit connection,
ventilation ports , standard patch cords (3meters)
and 25% reserve space for hubs and switches, with
fiber to copper converter, CAT 6, including screen,
| lable holder and all the necessary accessories.. | Nº | 2 | 21378.5 | 42757
G.Patch panel for PP-1F with 72 3U ports 8/4 contact
in fixed & 15U or approved equivalent swing 19"
steel enclosure with transparent and lockable door,
with corresponding power supply unit of 8pcs scuko
type socket out lets with power plug and standard
pivoting cabinet with rack for wall mounting , knock-
out holes for cable entrance and conduit connection,
ventilation ports , standard patch cords (3meters)
and 25% reserve space for hubs and switches, with
fiber to copper converter, CAT 6, including screen,
| lable holder and all the necessary accessories.. | Nº | 1 | 10689.25 | 10689.25
H.Patch panel for PP-1F with 96 4U ports 8/4 contact
in fixed & 15U or approved equivalent swing 19"
steel enclosure with transparent and lockable door,
with corresponding power supply unit of 8pcs scuko
type socket out lets with power plug and standard
pivoting cabinet with rack for wall mounting , knock-
out holes for cable entrance and conduit connection,
ventilation ports , standard patch cords (3meters)
and 25% reserve space for hubs and switches, with
fiber to copper converter, CAT 6, including screen,
| lable holder and all the necessary accessories.. | Nº | 2 | 21378.5 | 42757
I.Patch panel for PP-1F with 48 2U ports 8/4 contact
in fixed & 15U or approved equivalent swing 19"
steel enclosure with transparent and lockable door,
with corresponding power supply unit of 8pcs scuko
type socket out lets with power plug and standard
pivoting cabinet with rack for wall mounting , knock-
out holes for cable entrance and conduit connection,
ventilation ports , standard patch cords (3meters)
and 25% reserve space for hubs and switches, with
fiber to copper converter, CAT 6, including screen,
| lable holder and all the necessary accessories.. | Nº | 1 | 7400.25 | 7400.25
J.Patch panel for PP-2F with 120 5U ports 8/4 contact
in fixed & 15U or approved equivalent swing 19"
steel enclosure with transparent and lockable door,
with corresponding power supply unit of 8pcs scuko type
socket out lets with power plug and standard pivoting
cabinet with rack for wall mounting , knock-out holes for
cable entrance and conduit connection, ventilation ports ,
standard patch cords (3meters) and 25% reserve space for
hubs and switches, with fiber to copper converter,
CAT 6, including screen, lable holder ,complete connection
| with telephone cable and all the necessary accessories.. | Nº | 1 | 21378.5 | 21378.5
K.Patch panel for PP-2Fwith 96 4U ports 8/4 contact
in fixed & 15U or approved equivalent swing 19"
steel enclosure with transparent and lockable door,
with corresponding power supply unit of 8pcs scuko
type socket out lets with power plug and standard
pivoting cabinet with rack for wall mounting , knock-
out holes for cable entrance and conduit connection,
ventilation ports , standard patch cords (3meters)
and 25% reserve space for hubs and switches, with
fiber to copper converter, CAT 6, including screen,
lable holder ,complete connection with telephone
| cable and all the necessary accessories.. | Nº | 1 | 21378.5 | 21378.5
L.Patch panel for PP-BFwith 72 3U ports 8/4 contact
in fixed & 15U or approved equivalent swing 19"
steel enclosure with transparent and lockable door,
with corresponding power supply unit of 8pcs scuko
type socket out lets with power plug and standard
pivoting cabinet with rack for wall mounting , knock-
out holes for cable entrance and conduit connection,
ventilation ports , standard patch cords (3meters)
and 25% reserve space for hubs and switches, with
fiber to copper converter, CAT 6, including screen,
lable holder ,complete connection with telephone
| cable and all the necessary accessories.. | Nº | 1 | 10689.25 | 10689.25
M. Patch panel for PP-3F with 96 4U ports 8/4 contact
in fixed & 15U or approved equivalent swing 19"
steel enclosure with transparent and lockable door,
with corresponding power supply unit of 8pcs scuko
type socket out lets with power plug and standard
pivoting cabinet with rack for wall mounting , knock-
out holes for cable entrance and conduit connection,
ventilation ports , standard patch cords (3meters)
and 25% reserve space for hubs and switches, with
fiber to copper converter, CAT 6, including screen,
lable holder ,complete connection with telephone
| cable and all the necessary accessories.. | Nº | 2 | 21378.5 | 42757
N. Patch panel for PP-BF with72 3U ports 8/4 contact
in fixed & 15U or approved equivalent swing 19"
steel enclosure with transparent and lockable door,
with corresponding power supply unit of 8pcs scuko
type socket out lets with power plug and standard
pivoting cabinet with rack for wall mounting , knock-
out holes for cable entrance and conduit connection,
ventilation ports , standard patch cords (3meters)
and 25% reserve space for hubs and switches, with
fiber to copper converter, CAT 6, including screen,
lable holder ,complete connection with telephone
| cable and all the necessary accessories.. | Nº | 3 | 10689.25 | 32067.75
0.Patch panel for MPP with 96 4U ports 8/4 contact
in fixed & 42U or approved equivalent swing 19"
steel enclosure with transparent and lockable door,
with corresponding power supply unit of 8pcs scuko
type socket out lets with power plug and standard
pivoting cabinet with rack for wall mounting , knock-
out holes for cable entrance and conduit connection,
ventilation ports , standard patch cords (3meters)
and 25% reserve space for hubs and switches, with
fiber to copper converter, CAT 6, including screen,
lable holder ,complete connection with telephone
| cable and all the necessary accessories.. | Nº | 1 | 21378.5 | 21378.5
Hand drier
52 | Automatic Hand Drier Type VORTICE AHDR 19206
or equivalent of 220V/50HZ with heating temperature
of 40-60degree Celsius with dynamical balanced
centrifugal fan of multiple metallic vanes,
fire retardant, high gloss finish plastic cover and
mounting base, infrared sensors complete with
| all the accessories . | No | 8 | 7071.35 | 56570.8
TYPE OF LIGHT FITTINGS WITH LAMPS
Note: all light fittings should have appropriate
electric gear, lamps, mounting and other necessary accessories.
53 | Type 1
Mounting - ceiling surface
Lamp type- fluorescent T8
Number of Lamps -4
Reflector - sheet steel, white UV stabilized,
Diffuser- anti dazzle, vandal resistant poly carbonate
with prismatic faceting inside with smooth anti-
dust external surfaces
Lamp holder- poly carbonate with contacts in phosphor bronze
Lamp wattage-18watts
Luminare material-Steel sheet pressed in one piece
Ingress protection-20
Size -length 625mm ,width 625mm and height 65mm
| control gear-220V/50HZ, electronics ballast | Nº | 705 | 1151.15 | 811560.75
54 | Type 2
Mounting - ceiling surface
Lamp type- fluorescent T5
Number of Lamps -2
Optics- batten type
dark light louver high glossy,anti glare
Lamp holder- poly carbonate with contacts in phosphor bronze
Lamp wattage-36watts
Luminare material-Steel sheet pressed in one piece
Ingress protection-65
Size -length 1196mm ,width285 mm and height 70mm
| control gear-220V/50HZ, electronics ballast | Nº | 96 | 863.35 | 82881.6
56 | Type 3
Mounting - ceiling surface
Lamp type- TC-D
Number of Lamps -2
Optics- direct light
Lamp holder- poly carbonate with contacts in phosphor bronze
Lamp wattage-18 watts
Luminare material-cylindrical aluminium
Ingress protection-20
Size -length dia214mm and height 225mm
| control gear-220V/50HZ, | Nº | 164 | 370 | 60680
57 | Type 4
Mounting - wall surface
Lamp type-compact fluorescent
Lamp holder- poly carbonate with contacts in phosphor bronze
Number of Lamps -1
Lamp wattage-18watts
Luminare material-die-cast aluminuim
Ingress protection-65
Size -length 260,width 110mm and 75mm height
| control gear-220V/50HZ | Nº | 28 | 411.15 | 11512.2
58 | Type 5
Mounting - wall surface
Lamp type- fluorescent
Number of Lamps -1
Optics- prismatic
Lamp holder- poly carbonate with contacts in phosphor bronze
Lamp wattage-18 watts
Luminare material-Steel sheet pressed in one piece
Ingress protection-40
Size -length 670mm ,width120 mm and height 50mm
| control gear-220V/50HZ, electronics ballast | Nº | 5 | 781.15 | 3905.75
59 | Type E1
Mounting - wall surface
Lamp type- Emergency lamp of 2G7
Number of Lamps -1
Optics- Prismatic
Lamp holder- poly carbonate with contacts in phosphor bronze
Lamp wattage-8 watts/T5
Luminare material-steel sheet
Ingress protection-42
Size -length 356mm and width 136 mm
control gear-220V/50HZ,
| with 2 hour emergency battery kit | Nº | 71 | 1726.75 | 122599.25
60 | Type 6
Mounting - wall surface
Lamp type- fluorescent
Number of Lamps -1
Optics- prismatic
Lamp holder- poly carbonate with contacts in phosphor bronze
Lamp wattage-18 watts
Luminare material-Steel sheet pressed in one piece
Ingress protection-40
Size -length 670mm ,width120 mm and height 50mm
| control gear-220V/50HZ, electronics ballast | Nº | 5 | 805.8 | 4029
57 | Type 7
Mounting - ceiling surface
Lamp type- fluorescent
Number of Lamps -1
Reflector - sheet steel, white UV stabilized,
Diffuser- anti dazzle, vandal resistant poly carbonate
with prismatic faceting inside with smooth anti-
dust external surfaces
Lamp holder- poly carbonate with contacts in phosphor bronze
Lamp wattage-36watts
Luminare material-Steel sheet pressed in one piece
Ingress protection-40
Size -length 1245mm ,width 83mm and height 96mm
| control gear-220V/50HZ, electronics ballast | Nº | 27 | 904.5 | 24421.5
POWER CABLES
PVC sheathed PVC insulated cable rating of
0.6/ 1KV
58 | 2(3x300/150+150)mm2 | m | 120 | 5306.8 | 636816
59 | 5x16mm2 | m | 500 | 172.65 | 86325
60 | a.(5x25/16+16)mm2 | m | 300 | 301.75 | 90525
61 | b.5x10mm2 | m | 120 | 123.35 | 14802
62 | c.5x4mm2 | m | 100 | 65.8 | 6580
63 | d.(3x120/70+70)mm2 | m | 125 | 1085.35 | 135668.75
64 | e.5x6mm2 | m | 210 | 82.25 | 17272.5
65 | f.4x6mm2 | m | 80 | 57.55 | 4604
LIGHTNING PROTECTION
3rd party certified
Lightning protection equipment, supplied, installed,
connected, tested and commissioned including
conduits and all necessary accessories, complete
(or approved equivalent) and/or shown on drawings.
-Shall include all metallic structures in the network
with appropriate (CADWELD)welding (vent pipes,
ducts ,GIS roof& structures,AC units e.t.c)
Lightning preventor
Air termination network
Shall include all metallic structures in the network
with appropriate welding (ventpipes,ducts ,GIS roof&
structures,AC units e.t.c)
-Other than the air terminals it shall be25x3mm copper
tape with all the necessary accessories
-The network shall be secure fixed to the roof with brass
plate and phosprous screws every 500mm air terminals
shall be copper round end
66 | Air terminals h=3meters,20-30m range preventor head | No | 1 | 48438 | 48438
67 | 25x3mm copper tape | m | 300 | 427.55 | 128265
Down conductor
68 | 25x3mm copper tape with vertical
supporting every 1m to the wall & all the necessary
accessories coordinate the routing of down conductors
with the building external skin and architectural
| features | m | 300 | 394.7 | 118410
69 | 50 x 50 x 50 cm test pit with top cover inscribed
| "Test pit" as per the detail drawing | No | 12 | 4111.25 | 49335
70 | 25x3mm copper tape | m | 250 | 394.7 | 98675
71 | Earthing Electrode 65x65x7mm length 1500mm
| galvanized iron bracket | No | 12 | 2466.75 | 29601
UPS
with 3 years guarante
72 | Approved type Moudular type UPS APC , 3x380V+/-5%,
50Hz 120 KVA scalable to 160KVA with 10-min, hot
swappable sealed lead-acid battery 10 years ,on-line double
conversion technology, integrated automatic By-pass, manual
maintenance By-pass, automatic battery test, power factor 0.9,
efficiency 95% or greater, surge protector audio visual display
of load, battery and UPS status, input harmonic filter,
maintenance by-pass switch, all complete including
| cabling. | No | 1 | 98670 | 98670
CABLE WAYS AND MANHOLES
73 | Underground PVC pipes of diameter 200mm.
| Price to include cost all necessary accessories. | m | 150 | 246.7 | 37005
74 | Underground PVC pipes of diameter 50mm for
Tele intake. Price to include cost all necessary
| accessories. | m | 250 | 98.65 | 24662.5
75 | Rigid PVC pipes of diameter 80mm for feeder cable.
| Price to include cost all necessary accessories. | m | 125 | 156.25 | 19531.25
FIRE ALARM SYSTEM
Intelligent fire alarm equipment, supplied, installed,
connected, tested and commissioned including fire
rated cables, conduits and all necessary accessories,
complete as manufactured by Notifier/seimens
or approved equivalent and/or shown on drawings.
76 | Intelligent addressable fire control ,voice evacuation and indicating
panel, including Notification Appliance Circuit Modules,
Control Relay Module , auxilary contact and under
mentioned specification
-Input power 220VAC, 50 Hz
-Capable of networked connection
-Programmable internal hard ware and output circuits
-Programmable soft ware zones
-Accessories for out put connection for telephone circuit
-Sealed battery capable of supply to all equipments for
at least 72Hr
-Intelligent signaling line circuit
-voice alarm system interface
-Trouble acknowledge and alarm silence switch
-Visual and audiable trouble alarm by zone
-Manual acknowledge function
_Minimum of 40 zones digital
_LCD display (80 characters)
-Program keypad
-LED indicators
_15 relay outputs
_10 loops
-Compatible devices
-Compatible intelligent devices
with all necessary accessories as BSNE 54
| standards to make the system | No. | 1 | 323191.8 | 323191.8
77 | Loop powered Addressable Alphanumeric liquid
crystal display (LCD) type Annunciator c/w all
necessary mounting accessories, for surface/ flush.
| (location to be determine later) | No. | 3 | 16445 | 49335
78 | Intelligent photoelectric smoke sensors all necessary
| mounting accessories, for surface / flush | No. | 121 | 1936.7 | 234340.7
79 | Addressable manual pull switch station type all
| necessary mounting accessories, for surface / flush | No. | 23 | 1834.75 | 42199.25
80 | Loop powered Addressable detector/speaker / strobe (Red) c/w
| all necessary mounting accessories, for surface / flush. | No. | 20 | 1902.75 | 38055
81 | Power supply unit for beam detectors(optional) | No. | 1 | 6591.6 | 6591.6
82 | Loop powered Addressable reflective beam detector
| all necessary mounting accessories, surface mounted | No. | 19 | 2174.55 | 41316.45
83 | Addressable Manual pull switch station type or
equivalent c/w all necessary mounting accessories,
| mounted.for surface / flush. | No. | 6 | 1834.75 | 11008.5
84 | Loop powered Addressable detector/speaker / strobe (Red) c/w
| all necessary mounting accessories, for surface / flush. | No. | 2 | 1902.75 | 3805.5
FIRE ALARM POINTS
85 | Smoke / heat detector points fed through fire
resistant cable of 2-core 2.5sq.mm inside PVC
| conduit of 20mm diameter including all accessories. | No. | 123 | 515.8 | 63443.4
86 | Fire alarm speaker strobe points fed through fire
resistant cable of 4-core 1.5sq.mm twisted/shielded
inside PVC conduit of 25mm diameter including
| all accessories. | No. | 3 | 665.3 | 1995.9
87 | Manual call points fed through fire resistant cable
of 2-core2.5sq.mm inside PVC conduit of 20mm
| diameter including all accessories. | No. | 8 | 515.8 | 4126.4
88 | Reflective beam detector points fed through fire
resistant cable of 4-core 1.5sq.mm twisted/shielded
| inside PVC conduit of 25mmdiameter including all accessories. | No. | 19 | 665.3 | 12640.7
VOICE EVACUATION SYSTEM
voice evacuation equipment, supplied, installed, connected, tested
and commissioned including control speaker cables, conduits and all
necessary accessories, complete as manufactured and/or
shown on drawings.
89 | a.voice alarm controller
-6 zone system controller
- expandable up to 60 zones
- built in 240W booster amplifier
- digital pre-recorded messages
- emergency microphone input on the front panel
- 16 priority levels including emergency
-Individual BGM volume control for each zone
| -Standard and emergency control input and outputs | No. | 1 | 98670 | 98670
| b.Voice alarm 240W booster | No. | 1 | 11477.5 | 11477.5
| c.Voice alarm call stations | No. | 1 | 4546.15 | 4546.15
| d.Voice Alarm Remote Control Panel | No. | 1 | 44639.35 | 44639.35
| e.Voice Alarm BGM(back ground music source) | No. | 1 | 22214.35 | 22214.35
| f.Voice Alarm digital Message Manager | No. | 1 | 44639.35 | 44639.35
90 | Configuration/diagnostic & logging software | No. | 1 | 51006.7 | 51006.7
91 | 6W ceiling mounted speaker with fixing accessories
| and surface mounting box | No. | 45 | 5905.25 | 265736.25
92 | Softwares, documentation, instruction of
| owner's staff, power supplies. | LS | 1 | 20855.25 | 20855.25
93 | Floor standing 19" rack 585(W)x2000(H)x585(D)mm
| with glass door. | No. | 1 | 31048.45 | 31048.45
94 | Voice evacuation system points fed through audio cable of
PVC-insulated, A1-screened, twisted pair, 1sq.mm
stranded tinned copper wire, type Belden or approved
equivalent and in medium duty rigid thermospastic
conduit of minimum diameter of 16mm including
| junction box and all other fixing accessories. | No. | 45 | 515.85 | 23213.25
CCTV SYSTEM
Closed circuit television equipment, equipment
supplied, installed, connected, tested and
commissioned including coaxial cables, complete all
as specified (or equivalent) and/or shown on drawings.
95 | Purpose made control consol for eight 19"monitors,
| VCR, multiplexer, controller and keyboard | No. | 1 | 31395 | 31395
96 | Approved type POE Indoor color autodome PTZ
IR 32MB ,8MB, flush RS485 ,MPEG-4,
12X,1280x1024 ,32bit CPU IP surveillance
camera (0.005lux) price to include mounts and
(6mm/6mmMTVLense) mounting brackets including
| other necessary accessories resolution 480TV line. | No. | 42 | 18612.75 | 781735.5
97 | Approved type POE Indoor color autodome Fixed
IR 32MB ,8MB, flush RS485 ,MPEG-4,12X,
1280x1024 ,32bit CPU IP surveillance
camera (0.005lux) price to include mounts and
(6mm/6mmMTVLense) mounting brackets including
| other necessary accessories resolution 480TV line. | No. | 10 | 18612.75 | 186127.5
98 | Approved type12 port POE access switch with 220vac/50Hz
| memory of 64MB ,1GHz with 1terabyte HDD | No. | 4 | 25788.75 | 103155
99 | Approved type 48 channel NV(core switch) 220vac/50Hz |  |  |  | 0
| memory of 500MB ,1GHz with 40 terabyte HDD |  |  |  | 0
| pre loaded with all necessary licensed soft wares |  |  |  | 0
| will be done with no extra charg | No. | 1 | 133727.75 | 133727.75
100 | Approved type 24 channel NV(core switch) 220vac/50Hz |  |  |  | 0
memory of 500MB ,1GHz with 10 terabyte HDD
pre loaded with all necessary licensed soft wares
| will be done with no extra charg | No. | 5 | 52175.5 | 260877.5
101 | Approved server with RAM of 1GB with 100 Mb network
interface,10 terabyte HDD with mouse including
all softwares 8 port KVM switch,17" TFT screen,Rack
Mountable kit preloaded with all necessary
| licensed softwares will be don with noextra charg | No. | 2 | 123786 | 247572
102 | Licence softwares for CCTV and switch(NV) with complete
instruction preloaded to camera, server and switch all
| according to the requirement of manufactures all complete | L.S | 1 | 48662.25 | 48662.25
103 | softwares documentation,instracted of owner's
| staff, power supply | L.S | 1 | 21303.75 | 21303.75
104 | Approved tayp AV interface unit pre loaded with all
| the necessary licensed softwares will be done with no extra | No. | 1 | 1148.45 | 1148.45
charge
105 | Cat 6 24 port pach panel with cable organizer
| Rack Mountable | No. | 4 | 1148.45 | 4593.8
106 | fully programmable keyboard controller
| with touch screen LCD | No. | 4 | 1148.45 | 4593.8
PASSANGER LIFTS
107 | Supply install passenger lifts as per the following
specifications
a. Passenger Lift
Technical Specifications
Standards
ISO 7465:2001,EN-81,BS ,ANSI,JIS,ISO 9001,
ES 3158:2006,ES 3159:2006 , latest editions of BS/EN
or ES and others quality certificate for design, manufacturing
installation and commissioning lifts and quality certificate for design,
manfucturing,commissioning lifts parts.
-Electromagnetic compatibility
- Electromagnetic immunity
-Electrical Safety
- Electonic equipment for use in power facilities:
- Standards for lift installation in market places
Mechanical property and Finishing Material
Function :-Passenger Lift
Rated load : - 900kg, 13person
Rated speed :- 1.2m/sec
Number of stops:- 5 in one line
Floor - B+G + 3
Cabin door type:- Automatic single door center opening two panel
Landing door type:- Automatic single door center opening two panel
No entrance :- one(1) @ 0 degree
Floor - Vinyl composition tile/wear resistant rubber
Wall - Stainless steel on all side
Interior face of doors - Stainless steel
Ceilings - Stainless steel panels/diffuser gird
Handrail -stainless steel, two sides
Mirror -Silver color, rear panel
Frame- Stainless steel
Exterior face of door - Stainless steel
Drive system and Elevator operation
- Machine room less
- simplex Selective control
-Electric traction type
-VVVF with encoder
Special operation and facilities
- Smoke Detectors integrated with building fire alarm system
- Alarm buzzer
- Chime gong to sound present audioable indication
control
- Toggle switch
- call registered light
- Inter phone to communicate with machine room
- Over load indicator both audiable and visual indicators
Car and Landing operation panel
- Car display for position and direction
- Digital car position and direction control
-Digital landing position & direction indicator on
all floors
- lift movement control
-Vandal proof Wait/stop push button
-Car display for position and direction
Control and safety features
-Dynamic braking for traction machine in event of power
failure
Power supply
- 380volts AC 50Hz 3phase
Disable
- Add braille tactile to all emergency buttons
Lighting Supply
- 220v, 50Hz, 1ph
- Indirect light in diffuser grid
Ventilation
-Car ventilation with fan built in the ceiling
-Temperature control Thermostat
Rescue device
-Automatic rescue device/ back up when power fails
- All power outputs are electronically protected
against short circuit
- Earth leak detection for traction machine during
emergency operation(short circuit, overload, loss of
connection of a phase to the motor, phase imbalance,
thermal protection, over speeding, turning blockage)
Performs analysis of optimum motor turning direction
(minimum battery consumption during emergency
operation) Conforms to EN81 regulation
CCTV system
Provide passenger lifts appropriate type of camera
with its mounting accessories complete wiring and integrated
with the building security /CCTV system as per local and
international standards.
108 | Shaft Information
-Shall take and consider appropriate manufacturers' standards for
the shaft and machine room size before manufacturing .
and prepare working drawing referring to the arctectrural
and structural for submission with the technical specification.
coordinate with architectural and structural drawings during
constriction with appropriate changes with notice to comply
with the standards Submit for approval complete upto date
lift specification of the above items including guide rails,
suspension counter weight terminal stopping and final limit
switches, guarding car frames, safety gear and over speed governor
overload device and full load device, controller automatic control
system, reinforcement bar buffer, duty ,prewiring ,conducting/
trunking and other required and necessary specification
with working drawing referring to arctectural and structural
from at least 3 lift suppliers having a minimum of 3 years
or with equivalent grantee period in lift manufacturing ,design,
| installation and maintenance. | No | 1 | 1518000 | 1518000
109 | Thorn Voyager Status fluorescent wall mounting,
with 1x36W T8 or
| approved equivalent.(optional) | Nº | 10 | 1719.25 | 17192.5
ELECTRO MECHANICAL SYSTEM
Note: coordinate all Electrical installation with Mechanical
works.
Electrical connection for equipment controller, safety switch supplied,
installed, connected, tested and commissioned, including conduits,
cables, boxes complete al as specified and/or shown on drawings.
116 | Safety switch, Scame or approved equivalent,16A, 1poles with
| 1n/o auxiliary contact | No | 1 | 3064.75 | 3064.75
117 | Safety switch, Scame or approved equivalent, 16A, 3poles with
| 1n/o auxiliary contact . | No | 3 | 3064.75 | 9194.25
118 | Safety switch, Scame or approved equivalent,80A, 3poles with
| 1n/o auxiliary contact | No | 3 | 3812.25 | 11436.75
119 | Safety switch, Scame or approved equivalent,10A, 3poles with
| 1n/o auxiliary contact | No | 1 | 2911.5 | 2911.5
120 | Power supply for AC outdoor units insulated cable
of 5x4 mm2 in medium duty PVC conduit diameter
| of 80mm. | Nº | 2 | 8297.25 | 16594.5
121 | Power supply for ACindoor units insulated cable
of 3x2.5 mm2 in medium duty PVC conduit diameter
| of 19 mm. | Nº | 1 | 1569.75 | 1569.75
122 | Power supply for AC outdoor units insulated cable
of 5x4 mm2 in medium duty PVC conduit diameter
| of 21mm. | Nº | 1 | 8297.25 | 8297.25
123 | Power supply for AC chiler outdoor units insulated cable
of3x25/16mm2 in medium duty PVC conduit diameter
| of 80mm. | Nº | 3 | 7549.75 | 22649.25
124 | Control units connection for Exhaust fan motor as manufacturer
instruction 1ph fed by PVC insulated cable of 5x2.5mm2
| in medium duty PVC conduit diameter of 21mm. | Nº | 1 | 5307.25 | 5307.25
125 | Control units connection for Ceiling fan motor as manufacturer
instruction 1ph fed by PVC insulated cable of5x4mm2
| in medium duty PVC conduit diameter of 21mm. | Nº | 2 | 8297.25 | 16594.5
CABLE TRAY
-All cable tray shall run neatly and fixed in
contact with the horizontal and vertical corner
of the wall with the necessary drops and riser.
-The cable tray must consisting of accessories
like clamp kit,coupling plate ,cable mounting bracket ,
grounding cable drop out plate ,elbows and T-joints for
horizontal,bracket,mounting box support, suspension
bracketend cap, cable retainer, hinge connector for
vertical change in direction, wall and pendent bracket
for wall support ,box for cable junctions for all the
necessary accessories
126 | 100mmx500mm for power cables. Refer cable tray
| detail with ceiling installation drawing. | m | 260 | 306.5 | 79690
Man hole double brick wall with cast iron top
cover inscribed with"EL MH"
See the detail drawing
127 | Man hole80x80x100cm | Nº | 4 | 10062.5 | 40250
128 | Man hole70x70x90cm | Nº | 3 | 9027.5 | 27082.5
| TOTAL TO SUMMARY …………………… | BIRR |  |  | 11043123.3
SITE WORK
01.SANITARY INSTALLATION (includedin laboratory)
02.ELECTRICAL INSTALLATION (includedin laboratory)
03.WALK WAY & ASPHALT CONSTRUCTION
02. EXCAVATION & EARTH WORK
NB:- all excavation soil type according to the
attached soil report.
Bulk excavation
01 | To a depth not exceeding 50cm | m3 | 930 | 90.4 | 84072
Fill
02 | Selected borrowed fill
| (Compact until it attain 95% proctor density) | m3 | 788 | 136.6 | 107640.8
03 | fertial siol | m3 | 125 | 72.35 | 9043.75
04 | Disposal | m3 | 930 | 34.4 | 31992
Sub base
05 | 200 mm thick crushed agreggate | m2 | 685 | 132.45 | 90728.25
Concrete pavement ( for proposed raed aera)
06 | 8cm thick mass concrete in C-20 | m2 | 958 | 201.3 | 192845.4
Cement tile
07 | 8 cm thick fegured cement tile | m2 | 900 | 221.45 | 199305
Curb stone
Precast concrete in C-20 bedded on lean concrete
08 | Size:- 40x10cm | m | 360 | 264.5 | 95220
| TOTAL TO SUMMARY …………………… | BIRR |  |  | 810847.2